## RGF
Solidly Grounded Transformer
[6 empty] | RGF restraint | RGF Restraint after 1 cycle
Parameter | Typical Value | Value | Unit |  | Internal ground fault | 100%
Transformer Type | Delta/Wye 30deg |  |  |  | External phase A no CT saturation | 0%
Power | MVA | 2.5 | MVA |  | External phase A CT saturation | 90.48% | 49.08%
Phase-phase voltage | Winging1 | 50 | kV |  | External phase A CT saturation full load | 89.87% | 45.81%
| Winding2 | 11 | kV
Phase CT ratio | 600:5 | 200
Neutral CT Ratio | 200:5 | 200
Impedance | % | 6.33% | %
Fault point | % | 5% | %
Calculated Parameter | Parameter | Value | Unit
Load current | Irated | 131.216 | A
Fault current | If(max) | 2072.9221 | A
Fault point 5% | Ifault | 103.6461 | A
Ground diff pickup | IGD | 0.51823 | pu
Internal ground fault
Calculated Parameter | Parameter | Value | Unit | Equation
Primary fault current | IG | 0.51823 | pu | 37
Phase unit current | IA, B, C | 0.65608 | pu | 38
Symmetrical components | I1 | 0.65608 | pu | 39
| I2 | 0 | pu
| I0 | 0 | pu
Differential current | IG+IN | 0.51823 | pu | 40
IR1 | I1/8 | 0.08201 | pu | 45
IR2 | 3*I2 | 0 | pu | 46
IR0 | IG-IN | 0.51823 | pu | 47
IGD | IG+IN | 0.51823 | pu | 48
IGR | max(IR1, IR2, IR0) | 0.51823 | pu | 49
RGF restraint | IGD/IGR*100% | 100% | % | 50
External phase A no CT saturation
IA | If(max)/PhCTratio | 10.3646 | pu
IB | If(max)/PhCTratio | 0 | pu
IC | If(max)/PhCTratio | 0 | pu
IN | If(max)/NCTratio | 10.3646 | pu
IG | If(max)/NCTratio | 10.3646 | pu
I1 | I1=I2=I0 | 3.4549 | pu
I2 |  | 3.4549 | pu
I0 |  | 3.4549 | pu
IGD | IG+IN | 0 | pu
IR1 |  | 0 |  | 53
IR2 |  | 10.3646 |  | 54
IR0 | IG-IN | 20.7292 | pu | 55
IGR | max(IR1, IR2, IR0) | 20.7292 | pu | 56
RGF restraint | IGD/IGR*100% | 0% | % | 57
External phase A CT saturation
IA | If(max)/PhCTratio | 10.3646 | pu
IB | If(max)/PhCTratio | 0 | pu
IC | If(max)/PhCTratio | 0 | pu
IN | If(max)/NCTratio | 10.3646 | pu
IG | If(max)/NCTratio | 0.51823 | pu
I1 | I1=I2=I0 | 3.4549 | pu
I2 |  | 3.4549 | pu
I0 |  | 3.4549 | pu
IGD | IG+IN | 9.8464 | pu
IR1 |  | 0
IR2 |  | 10.3646
IR0 | IG-IN | 10.8828 | pu
IGR | max(IR1, IR2, IR0) | 10.8828 | pu
RGF restraint | IGD/IGR*100% | 90.48% | %
RGF restraint | IGD/IGR*100% | 49.08% | %
External phase A CT saturation full load
IA | If(max)/PhCTratio | 10.3646 | pu
IB | If(max)/PhCTratio | 0.65608 | pu
IC | If(max)/PhCTratio | 0.65608 | pu
IN | If(max)/NCTratio | 9.7085 | pu
IG | If(max)/NCTratio | 0.51823 | pu
I1 |  | 3.892 | pu
I2 |  | 3.236 | pu
I0 |  | 3.236 | pu
IGD | IG+IN | 9.1903 | pu
IR1 |  | 1.968 | pu
IR2 |  | 9.708
IR0 | IG-IN | 10.2268 | pu
IGR | max(IR1, IR2, IR0) | 10.2268 | pu
RGF restraint | IGD/IGR*100% | 89.87% | %
RGF restraint | IGD/IGR*100% | 45.81% | %

## Symmetrical Components
Decomposition of Three-phase Vector System into its Symetrical Componenets
Original Vector System
| Name | Magnitude | Angle
|  |  | [°] | [rad]
| A | 10.3646 | 0 | 0
| B | 0.65608 | -120 | -2.0944
| C | 0.65608 | -240 | -4.1888
| N | 9.7085 | 0 | 0
Input known vectors here
Conversion to Cartesian Coordinates for Chart
| Vector |  |  |  | Complex Number
| Name | Point | Coordinates
|  |  | X | Y | a + bi
| A | Origin | 9.7085 | 0 | 10.365
|  | End | 20.0731 | 0
| B | Origin | 9.7085 | 0 | -0.328-0.568i
|  | End | 9.3805 | -0.56818
| C | Origin | 9.7085 | 0 | -0.328+0.568i
|  | End | 9.3805 | 0.56818
| N | Origin | 0 | 0 | 9.709
|  | End | 9.7085 | 0
Symetrical Component Vectors
| Vector |  |  |  | Complex Number | Phasor
| Name | Point | Coordinates |  |  | Magnitude | Angle
|  |  | X | Y | a + bi |  | ° | rad
Definition of Unit Vector
| a | End | -0.5 | 0.86603 | -0.5+0.866i | 1 | 120 | 2.0944
| a^2 | End | -0.5 | -0.86603 | -0.5-0.866i | 1 | 240 | 4.1888
Zero Sequence Vectors
| A(0) | Origin | 16.8365 | 0 | 3.236 | 3.236 | 0 | 0
| (0) | End | 20.0725 | 0
| B(0) | Origin | 6.1445 | -0.568 | 3.236 | 3.236 | 0 | 0
|  | End | 9.3805 | -0.568
| C(0) | Origin | 6.1445 | 0.568 | 3.236 | 3.236 | 0 | 0
|  | End | 9.3805 | 0.568
Positive Sequence Vectors
| A(+) | Origin | 9.7085 | 0 | 3.892 | 3.892 | 0 | 0
| (0) | End | 13.6005 | 0
| B(+) | Origin | 9.7085 | 0 | -1.946-3.37i | 3.8915 | -120.0042 | -2.0945
|  | End | 7.7625 | -3.37
| C(+) | Origin | 9.7085 | 0 | -1.946+3.37i | 3.8915 | 120.0042 | 2.0945
|  | End | 7.7625 | 3.37
Negative Sequence Vectors
| A(-) | Origin | 13.6005 | 0 | 3.236 | 3.236 | 0 | 0
| (0) | End | 16.8365 | 0
| B(-) | Origin | 7.7625 | -3.37 | -1.618+2.802i | 3.2356 | 120.0041 | 2.0945
|  | End | 6.1445 | -0.568
| C(-) | Origin | 7.7625 | 3.37 | -1.618-2.802i | 3.2356 | -120.0041 | -2.0945
|  | End | 6.1445 | 0.568